BENEFITS OF POWER FACTOR IMPROVEMENT

Most benefits provided by a power factor improvement system from the reduction of reactive power in the system. This may result in

A) Lower purchased-power cost if the utility enforces a power-factor clause
B) Release of system electrical capacity
C) Voltage improvement and
D) Lower system losses

Maximum benefits are obtained when capacitors are located at low power-factor levels. Although reducing the power bill is still primary reason for improving the power factor, and it is becoming more important because of conservation of energy, the function of releasing system capacity is sometimes the decisive factor.

2. POWER-FACTOR FUNDAMENTALS:

Causes of Low Power Factor.

Most utilization devices require two components of current.

a) The power producing current or working current is that current which is converted by the equipment into useful work, usually in the form of heat, light or mechanical power. The unit of measurement of power is WATT.

b) Magnetizing current, also known as Watt-less, reactive or non-working current, is the current required to produce the flux necessary for the operation of electromagnetic devices. Without magnetizing current, energy could not flow through the core of transformer. The unit of measurement of reactive power is VAR.

The normal relationship of these two components of current to each other, to the total current, and to the system voltage is explained in Fig-1. It shows that the active current and reactive current add vectorially to form the total current which can be determined from the expression,

Total current = I = √(ICos Φ	)2 + (ISin Φ	)2

Where ICos Φ	 = Active current and ISin Φ	 = Reactive current

At a given voltage, V, the active, reactive and apparent power are proportional to current and are related as follows:

VI =((VICos Φ	)2 + (VISin Φ	)2)1/2

Where VI = apparent power, VI Cosj = Active power, VI Sinj  =  Reactive power

3. DEFINITION OF POWER-FACTOR:

The power factor is defined as the ratio of active power to apparent power in a circuit. It varies from one to zero but is generally given as below:

Power factor = Active power in KW / Apparent power KVA

Power Factor = cosine of angle between active power and       apparent power

= Cos Φ

Active Power = Apparent power × Power Factor

= (KVA). (PF)

4. LEADING AND LAGGING POWER FACTOR:

The power factor may be lagging or leading depending on the direction of both the active and reactive power flows. If these flows are in same direction, the power factor at that point of reference is lagging. If either power component flow is in an opposite direction, the power factor at that point of reference is leading. Since the capacitors are a source of reactive power only, their power factor is always leading. An induction motor or transformer has a lagging power factor as it required both active and reactive power into in the motor or transformer.(same direction)

5. BASIC POWER FACTOR ECONOMICS:

High plant power factors can yield direct savings. Some, such as reduced power bills and release of system capacity, are quite visible; others, such as decreased I2R losses (copper loss) are also visible. The cost of improving the power factor in existing plants, and of maintaining proper levels as load is added, depends on the power factor value selected and upon the equipment chosen to supply the compensating reactive power. In general, medium voltage capacitors cost less per kilovar than low-voltage capacitors.

The combination of reduced power billing and released system capacity by improving the power factor is very attractive economically.

On comparing the installation cost of power factor improving capacitors and installed cost per KVA of power distribution equipment, it is achieved that the economic power factor would be 0.95

6. HOW THE POWER FACTOR IS IMPROVED:

When the reactive power component in a circuit is reduced, the total current is reduced. If the active power component does not change, as is usually true, the power factor will improve as the reactive power component becomes zero, the power factor will be unit or 100 percent.

Suppose a transformer load (in the power plant used in DOT) takes an active load of 80A and a reactive load of 60A from the mains, the total or line current will be of v802 + 1002 = 100 Amps. If a capacitor is installed so that it will supply the reactive current of 60A, then the supply needs to deliver only 80A to the exactly same load of the transformer. The supply circuit is now carrying only active power, hence the system capacity is not wasted in carrying reactive power.

Now, if we increase the capacity of capacitor further to increase the reactive current, the excess reactive current tends to flow towards the mains, causing the leading power-factor, which is also not advisable in the view of Electricity authorities.

Calculation of methods of power-factor improvement.

From the right triangle relationship shown in Fig.1, the simple and useful mathematical expressions may be written.

Cos Φ	= Active Power        =  KW           		   -EQ:1

Apparent Power       KVA

Tan Φ  = Reactive Power     =Kvar			    -EQ:2

Active power	        KW

Sin Φ = Reactive power       =Kvar             		    -EQ:3

Apparent power        KVA

Because the active power component usually remains constant and the apparent power and reactive power components change with the power factor, the expression involving the active power component is the most convenient one to analyse. This expression may be written as

Reactive Power = Active power  × Tan Φ

Kvar   =  (KW). Tan Φ	    			-EQ:4

Where Tan Φ corresponds to the power factor angle.

For example, assume that it is necessary to determine the Capacitor rating to improve the load power factor:

Reactive power at  Original power factor = Active power  × Tan Φ1

= (KW).( TanΦ1)			   -EQ:5

Reactive power at Improved power factor = Active power × Tan Φ2

= (KW).( Tan Φ2)		  - EQ6

Where the Φ1= angle of original power factor

Φ2= angle of improved power factor

Therefore the capacitor rating required to improve the power factor is

Reactive power of capacitor   = Active power  × (Tan Φ1  -  Tan Φ2 )

‘Kvar ‘  Rating of the capacitor

=(KW). (Tan Φ1  -  Tan Φ2 )                                     -EQ:7

Example:  Find the capacitor rating required to improve the power factor of a 50KW load from 0.76 to 0.93

Kvar   = KW.  (Tan Φ1  -  Tan Φ2 )

Cos Φ1 = 0.76;    Φ1 = 40º 54’ : Tan Φ1 = 0.8662

Cos Φ2  =0.93;   Φ2 =21º 38’ : Tan Φ2	=0.3966

Tan Φ1  -  Tan Φ2    = 0.4676

Now Kvar  =  50 (0.4696)     =    23.48      	d 25 Kvar

Capacitor rating  =  25 Kvar

7.LOCATION OF REACTIVE POWER SUPPLY:

The benefits obtained by installing capacitors for power factor improvement result from the reduction of reactive power in the system. They should, in general, be installed as cloase to the load as possible. It is in common practice to connect the capacitors ahead of individual plants. This provides power factor improvement at the load and permits switching the capacitor and the plant as a unit as shown in location C1 of fig.3.

Power factor improvement for small loads or for those units that for some other reason may not lend themselves to have capacitors directly associated with the load, may be accomplished by connecting capacitors at a substation at location C2.

Large plants with extensive primary distribution systems often install capacitors at the primary voltage bus at location C3 when the utility billing encourages the user to improve the power factor.

  - Fig 3

8.RELEASE OF SYSTEM CAPACITY

The expression, release of capacity means that as the power factor is improved, the current in the existing system will be readuced, permitting additional load to be served by the same system.

If a plant has a load of 100KVA at 70 percent power factor and 48 Kvar of capacitors are added, the system electric capacity is released by 28 percent approximately, that the system can carry 28 percent more load without exceeding the apparent power rating. The final power factor of the original load plus the additional load will be 0.9 (90 percent) approximately.

9.VOLTAGE IMPROVEMENT

Although capacitors raise a circuit voltage, it is rarely economical to apply them in industrial plants for that reason alone. The following approximate expression shows the importance of reducing the reactive power component of a current in order to reduce the voltage drop.

∆V  ≈  RI cos Ф ± XI sin Ф

∆V = ( R) X [Active power current] ±(X ) [Reactive power current]

Where ∆V  is the voltage change, which may be a drop or rise in voltage;

R  and  X  are in ohms;  I  in amperes; Ф  is the power factor angle. Plus is used when the power is lagging and minus when it is leading.

Typically, reactive power flow produces a voltage drop. Since the power factor acts directly to reduce reactive power flow, it is most effective in reducing voltage drop.

10. POWER SYSTEM LOSSES:

Although the financial return from conductor loss reduction is seldom sufficient to justify the installation of capacitors, it is an attractive additional benefit. System conductor losses are proportional to current squared, and since current is reduced in direct proportion to power factor improvement, the losses are inversely porportional to the square of the power factor.

Percentage loss reduction =   100 [1 – (Original PF / Improved PF)2 ]

Case Study of Usage of Capacitor banks for Improving PF - TE Harbour

1.When all the capacitors are switched OFF,

PF : 0.787            KVA : 414.3		KW : 326.1

2. KVAR required to improve the PF to 0.9  = 326.1 x 0.292 (MF) = 95.22

= 95 KVAR

3. KVAR required to improve the PF to 1.0  = 326.1 x 0.776 (MF)   = 253 KVAR

4.Additional KVAR required to improve the PF from 0.9 to 1.0

= 253-95 =158 KVAR

5.Capital Investment for installing Capacitors:

- Cost of capacitor with MS compartment & switch gears

Per   KVAR =  Rs.1500

Total amount for 158 KVAR  = 158 x 1500 = Rs.2,37,000 ----- (A)

- Watt loss of the capacitor = 0.5 W per KVAR

For 158 KVAR , the total watt loss = 0.5 x 158 = 79 W

Expenditure on electricity charges

Per month @ Rs. 5 /Unit         = 79 x24 x5 x30 =Rs.284---(B)

1000

| Sl No | Bill period from 4/2004 to 9/2004 | Actual Maximum Demand | Actual Power Factor | No. of units consumed |
| --- | --- | --- | --- | --- |
| 1 | April | 568.9 | 0.99 | 320,620 |
| 2 | May | 602.0 | 1.0 | 312,230 |
| 3 | June | 554.7 | 1.0 | 306,910 |
| 4 | July | 542.8 | 0.99 | 264,550 |
| 5 | August | 482.3 | 0.99 | 240,210 |
| 6 | September | 551.9 | 0.98 | 223,330 |
|  | Average /Month | 550 |  | 2,77,925 |

Contract demand : 700 KVA

- Electricity Charges for a month if PF = 0.9

  - Unit Charges @ Rs.5/unit     = 2,77,925 x 5 = 13,89,625

  - MD charges @ Rs. 300 /KVA = 630 x 300     =  1,89,000

------------

15,78,625—©

- Electricity Charges for a month if PF = 1.0

  - Unit Charges @ Rs.5/unit     = 2,77,925 x 5 = 13,89,625

  - MD charges @ Rs. 300 /KVA = 630 x 300     =  1,89,000

------------

15,78,625

------------

  - Rebate @ 2.5 %						39,466

-----------

15,39,159—(D)

-----------

5. Rate of return of cost of Capacitors

| Month | Interest on the investment made @ 5 % PA | Expenditure due to watt loss of capacitor | Return of cost due to incentive | Balance amt. to be recovered |
| --- | --- | --- | --- | --- |
| 0 | 0 | 0 | 0 | 237,000 |
| 1 | 995 | 284 | 39,466 | 198,813 |
| 2 | 835 | 284 | 39,466 | 160,466 |
| 3 | 674 | 284 | 39,466 | 121,958 |
| 4 | 512 | 284 | 39,466 | 83,289 |
| 5 | 350 | 284 | 39,466 | 44,456 |
| 6 | 187 | 284 | 39,466 | 5,461 |

  - Approximately in 6 months time the cost of capacitors are paid back by means of incentive.